[image: image1.jpg]CleaverBrooks’ )ﬁi’





SUGGESTED SPECIFICATIONS – MODEL XLG
NATURAL GAS ONLY BURNERS
Furnish and install       C-B ProFire gas burner(s), Model XLG      .  Each burner shall be a multi-port type capable of burning       C.F.H.       B.T.U. per cu. ft.       gas at a pressure of       (P.S.I.) (in W.C.) at the inlet to the gas control train, with a minimum turndown ratio of       to     . 

The burner shall be capable of firing against a furnace pressure from a negative .05 to a positive       in. W.C. without a reduction in capacity or efficiency.  The blower motor is to be       h.p., 3450 r.p.m. for 900 to 1,500 BHP and       h.p., 1800 r.p.m. for 1,600 to 2,200 BHP,       volts,       phase,       hertz, directly driving a backward-curved impeller to supply all air for combustion.  Combustion air volume shall be controlled by multiple air louvers with an air silencer assembly.  The burner shall have a hinged rear-access cover to swing away allowing easy access to the burner head components.  

The remote control panel shall include an electronic combustion flame safeguard programmer model       or,       for flame supervision, motor starters with overloads and 3-leg protection for 3-phase motors, ignition transformer, operating switches, signal lights, and color-coded / numbered wiring.  The control circuit shall be 120 volts, 60 hertz, single phase, supplied by a separate circuit or an adequate control circuit transformer.  A junction box shall be burner mounted for connection to the remote control panel.  The combustion control system shall incorporate full electric modulation.

The gas train(s) shall conform to UL (Option: GE Gap, NFPA-85, FM, and CSD-1, or other regulatory bodies), specifications and shall include all necessary safety shutoff valve(s), manual shutoff valve(s), high and low gas pressure switches, pressure regulator, vent valve and pressure gauge.

Ignition shall be of the interrupted gas-electric type.  A pilot shutoff cock, gas pressure regulator and automatic pilot gas valve shall be provided for each burner.

Knowing that the basic function of a burner is to mix fuel with air, the burner shall be of the high mixing rate type to insure that the flame dimensions are minimized to fit the combustion chamber.  The mixing efficiency of the burner shall be such that the burner will be able to achieve complete combustion with optimum stoichiometry to achieve the lowest possible emissions and optimum boiler efficiency.  Complete combustion is defined as less than 100 ppm of CO.

The burner throat shall be fully metallic and straight cylindrical for maximum air-cooling effect.  A divergent refractory throat that results in loss of air mixing velocity, and leads the airflow to widen at burner outlet and causing flame impingement on sidewalls, will not be accepted.

The igniter shall be gas-electric and provide sufficient ignition heat input using either natural gas or propane.  

The igniter shall meet NFPA Class III requirements.

The igniter shall be supplied complete with gas hose and flexible electrical harness assembly connecting the igniter spark plug to the ignition transformer.

The igniter shall use combustion air from the burner forced draft fan and not require an independent source of combustion air.  No flame rods shall be used for igniter flame detection.

Page 1 of 1                                                   
CB-8282



10/10

