[image: image1.jpg]CleaverBrooks’ )ﬁi’





SUGGESTED SPECIFICATIONS – MODEL Q
NATURAL GAS ONLY BURNERS
Furnish and install       C-B ProFire gas burner(s), Model Q     . The complete burner shall be listed with Underwriters’ Laboratories, Inc., bear the UL label and shall be completely assembled, wired and factory tested.  (Option: The burner shall meet the requirements of GAP, NFPA-85, FM, and CSD-1, or other regulatory bodies.)  Each burner shall be a forced draft fuel-air type at a maximum firing rate of       C.F.H. of       B.T.U. per cu. ft.       gas at a pressure of       (P.S.I.) (in. W.C.) at the inlet to the gas control train.
The burner blower shall be a centrifugal axial air flow type capable of firing at full rating against a furnace pressure from a negative .05 to a positive       in. W.C. without a reduction in capacity or efficiency.  The blower motor is to be a DC motor with pulse width modulation       volts,       phase,       hertz, directly driving a back-ward-curved impeller, with self-cleaning vanes to supply all air for combustion. 

The burner mounted control panel shall include an electronic combustion flame safeguard programmer model       or,       for ultra-violet flame supervision, relays or motor starter(s), ignition transformer, operating switches, four signal lights (power on, main fuel, ignition, flame failure), and color-coded wiring.  The control circuit shall be 120 volts, single phase, 60 hertz, supplied by a separate circuit or an adequate control circuit transformer.

The combustion control system shall incorporate full modulation, using pulse width modulation and parallel positioning for gas control.  There should be no air damper assembly required.
The gas train(s) shall conform to UL (Option: GAP, F.M., or other regulatory bodies) specifications and shall include all necessary safety shutoff valve(s), manual shutoff valve(s), high and low gas pressure switches, pressure regulator, vent valve and pressure gauge.

Ignition shall be of the direct spark type and an ignition transformer shall be provided for each burner.  The ignition and flame rod or UV scanner shall be mounted on the main drawer assembly and be removable from the external side of the burner.

Page 1 of 1                                                   
CB-8422


02/14

