[image: image1.jpg]CleaverBrooks’ )ﬁi’



CBEX ELITE

1,300 – 2,200 HP


Sample Specifications

Model CBEX Elite 1300-2200 HP

Boiler Characteristics (Steam)
2

General Boiler Design
2

Steam Boiler Trim
3

Burner
4

Fuel Specification and Piping
5
Boiler Controls and Control Panel
8
Efficiency Guarantee
8
Warranty Shop Tests
8 

SAMPLE SPECIFICATIONS

The following sample specifications are provided by Cleaver-Brooks to assist you in meeting your customer’s specific needs and application.

Detailed burner specifications are provided. See Boiler Book Controls section for additional information on control options. The Sample Specifications are typically utilized as the base template for the complete boiler specification. Contact your local Cleaver-Brooks authorized representative for information on special insurance requirements, special code requirements, optional equipment, or general assistance in completing the specification.

PART I
GENERAL

CBEX Elite Steam Boiler 1300-2200 HP

(1300-1600  hp — 50-250 psig steam) 
(1800-2000  hp — 50-200 psig steam) 
(2200 hp — 190 psig steam)

1.1 
BOILER CHARACTERISTICS (STEAM)

A.
The Steam Boiler shall be Cleaver-Brooks Fuel Series  
(100, 200, 700),  

hp designed for  
psig (50, 150, 190, 200, or 250 psig steam). The maximum operating pressure shall be  

psig and the minimum operating pressure shall be  
psig.

B.
The boiler shall have a maximum output of  
Btu/hr, or  
horsepower when fired with CS12-48 #2  oil and/or natural gas,  
Btu/cu-ft. Electrical power available shall be  
 Volt  
Phase  
Cycle.
PART 2 
PRODUCTS

2.1 
GENERAL BOILER DESIGN
A.
The boiler shall be a two pass horizontal firetube updraft boiler with  
square feet of heating surface per rated boiler horsepower. It shall be mounted on a heavy steel frame with integral forced draft burner and burner controls.

1. 
The boiler shall be completely preassembled and fire tested at the factory. The unit shall be ready for immediate mounting on floor or simple foundation and ready for attachment of water, fuel, electrical, vent, and blowdown connections.

2. 
The boiler shall be built to comply with the following insurance and codes  
 (Factory Mutual, XL GAP, ASME, NFPA 8501).

B.
Boiler Shell (Steam)

1. 
The boiler shell must be constructed in accordance with ASME Boiler Code and must receive authorized boiler inspection prior to shipment. A copy of the inspection report shall be furnished to the purchaser.

2. 
The boiler shall be furnished with a manhole and handholes to facilitate boiler inspection and cleaning. Two lifting lugs must be located on top of the boiler.

3. 
The front smokebox doors shall be davited and sealed with superwool insulation and fastened tightly using locking lugs on steel studs.

4. 
The rear door shall be fitted with an access plug for rear fireside inspection.

5. 
The boiler tubes shall not include turbulators, swirlers, or other add-on appurtenances.

6. 
The exhaust gas vent shall be located at the front of the boiler and be capable of supporting 2000 lbs. The boiler vent shall contain a stack thermometer.

7. 
Observation ports for the inspection of flame conditions shall be provided at each end of the boiler.

8. 
The boiler insulation shall consist of 2 inch blanket under a sectional pre-formed sheet metal lagging. The insulation must be readily removable and capable of being reinstalled if required.

9. 
The entire boiler base frame and other components shall be factory painted before shipment, using a hard-finish enamel coating.

10.  
The boiler shall contain a chemical feed connection.

2.2 
STEAM BOILER TRIM

A.
Water Column/low Water Cutoff And Water Level Control System shall be a CB LEVEL MASTER water level control system and shall comprise a microprocessor-based electronic controller, a non-contact, non-wearing, continuously reading absolute level sensor, and pressure chamber. The control system shall be designed as follows: The electronic controller shall be mounted in the common control panel and operate in ambient temperatures from 32 degrees F to 125 degrees F. The pressure chamber shall be boiler mounted and operate to pressures of 250 PSIG and the level sensor shall operate to pressures of 250 PSIG and temperatures to 400 degrees F. The pressure-containing components shall be constructed in accordance with ASME Code. A shielded, four conductor cable with ground shall be run in metal conduit between the level sensor and the controller. Supply power shall be 115VAC-1 phase- 60 Hz. All wiring shall be in compliance with the National Electrical Code.

The pressure chamber shall have a sight glass mounted on the side. The level sensor shall have an accuracy of 0.01” or greater. The electronic controller shall have level and error indicating lights, alphanumeric display for messaging, reset/ menu switch and the following features:

a.
Continuous Level Indication 
b.
Low Water Cutoff & Alarm 
c.
High Water Alarm

d.
Low & High Water Warning

e.
Full Modulating Control of Modulating Feedwater Control Valve 
f. 
Continuous Monitoring of Float Operation

g.
Column Blowdown Detection and Reminder 
h. 
Auto or Manual Reset

i. 
Real Time Clock

j. 
Alarm Annunciation

k. 
Alarm History Files with Time Stamp 
l. 
Water Column Blowdown Record

m. 
Auxiliary Low Water Cutoff Check 
n.
RS 232 Interface

Maximum Contacts Rating 15 amps Resistive Load

B.
Modulating feedwater Control

The boiler modulating feedwater control and valve shall be included to automatically maintain the boiler water level within normal limits.

C.
Auxiliary Low Water Cut-off
Auxiliary low water cut-off shall be included, piped to the vessel, and wired to the burner control circuit. A manual reset device shall be used on this control.

D.
Steam Pressure Gauge

The steam pressure gauge shall be located at the front of the boiler and include cock and test connection.
E.
Safety Valves

Safety valves of a type and size to comply with ASME Code requirements shall be shipped loose.

F.
Steam Pressure Controls

The steam pressure control to regulate burner operation shall be mounted near the water column. Controls shall be a high limit (manual reset), operating limit (auto reset), and firing rate control.
2.3 
BURNER

A.
Mode of Operation

1. 
Burner operation shall be full modulation principle. The burner shall always return to low fire position for ignition.

2. 
A low fire hold temperature control is mounted and wired on the boiler. 
B.
Blower

1. 
Air for combustion shall be supplied by a forced draft blower mounted on the burner, to eliminate vibration and reduce noise level.

2. 
Maximum sound level of the boiler/burner package shall not exceed  
dbA (when measured in accordance with ABMA Sound Test Standards).

3. 
The impeller shall be fabricated steel with radial blade, carefully balanced, and directly connected to the blower motor shaft.

C.
Combustion Air Control

Combustion air damper and fuel metering valve shall be operated by individual actuators to regulate the flame according to load demand.

2.4 
FUEL SPECIFICATION AND PIPING

Select one of the following fuel types:

• Fuel series 700 - Gas-fired.

• Fuel series 100 - Light oil (No. 2) fired.

• Fuel series 200 - Light oil or gas-fired.

A.
Fuel Series 700 - Gas-Fired

1. 
Burner type - The burner shall be mounted at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.

2. 
Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).

3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.

4. 
Burner Turndown: Turndown range shall be 8:1 when firing natural gas (consult with Cleaver-Brooks representative regarding high turndown capability based on available gas pressure).

B.
Fuel Series 100 - Light Oil-Fired

1. 
Burner type - The burner shall be mounted at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.

2. 
Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).

3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided.

4. 
Oil Burner Piping

a.
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit.

5. 
Low Pressure Air Atomizing: separate air compressor module, shipped loose, with burner mounted low atomizing air pressure switch.

6. 
Turndown range shall be 6:1 when firing No. 2 oil.

C.
Fuel Series 200 - Light Oil or Gas-Fired

1. 
Burner type - The burner shall be mounted at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.

2. 
Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).

3. 
Oil Burner

a.
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank.

b.
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit.

c.
Low pressure air atomizing - Separate air compressor module, shipped loose with burner-mounted low-atomizing air pressure switch.

d.
Burner Turndown - Turndown range shall be 6:1 when firing No. 2 oil.

4. 
Gas Burner

a.
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.

b.
Burner Turndown - Turndown range shall be 8:1 when firing natural gas.

2.5 
BOILER CONTROLS AND CONTROL PANEL

A.
Control/Entrance Panel - A common enclosure shall house the control panel and the entrance panel. Enclosure shall be NEMA 4/12 rated and shall be mounted at the side of the boiler in a location convenient to the operator. Enclosure shall consist of upper and lower sections divided by a partition with a separate hinged door for each section. Upper section (low voltage) will house boiler controls including flame safeguard and water level system controller. Lower panel section (high voltage) will house entrance panel.

B.
Cleaver Brooks Combustion Control System - Parallel positioning with separate actuators for each fuel and combustion air shall be used to provide proper fuel air ratio control.

C.
CB780E Flame Safeguard - Each boiler shall be factory equipped with flame safeguard controller providing technology and functions equal to the Cleaver- Brooks Model CB780E.
Oil, heat and moisture resistant wire shall be used and identified with circuit numbers corresponding to the electrical wiring diagram.

Boiler to be supplied with a control circuit transformer and fuse protection for the control circuit.

2.6 
EFFICIENCY GUARANTEE

A.
The boiler must be guaranteed to operate at a minimum fuel-to-steam efficiency of  
percent at 100 percent of rating when burning natural gas and fuel-to-steam efficiency at 100% firing rate when burning oil (Contact your local Cleaver-Brooks authorized representative for efficiency details).

PART 3
EXECUTION
3.1 
WARRANTY

A. 
All equipment is to be guaranteed against defects in materials and/or workmanship for a period of 12 months from date of start-up, or 18 months from date of shipment; whichever comes first.

3.2 
SHOP TESTS

A.
The packaged boiler must receive factory tests to check the construction, controls, and operation of the unit. All tests may be witnessed by the purchaser, if desired.

B.
Start-up Service

1. 
After boiler installation is completed, the manufacturer shall provide the services of a field representative for starting the unit and training the operator at no additional costs.

2. 
A factory-approved and authorized start-up report shall be submitted to the customer/user at the time of start-up.





4
Rev. 04-11

