[image: image1.png]CleaverBrooks’ b



Model (ie. Model CFV)


Group (ie. Commercial Boilers

Model CBL


900-1800 HP Boilers

Sample Specifications Model CBL
22PART 1 
GENERAL
A5-

221.1 
Boiler Characteristics (Steam)
A5-

22PART 2 
PRODUCTS
A5-

222.1 
General Boiler Design
A5-

232.2 
Steam Boiler Trim
A5-

232.3 
Burner and Controls
A5-

242.4 
Fuel Specification and Piping
A5-

272.5 
Boiler Flame Safeguard Controller and Control Panel
A5-

272.6 
Efficiency Guarantee
A5-

27PART 3 
EXECUTION
A5-

273.1 
Warranty
A5-

273.2 
Shop Tests
A5-



SAMPLE SPECIFICATIONS

The following sample specifications are provided by Cleaver-Brooks to assist you in meeting your customer’s specific needs and application.

The detailed burner and control specifications, and detailed control specifications for CB100E Flame Safeguard control are provided. See Section D, Controls, for additional information on control options.

The Sample Specifications are typically utilized as the base template for the complete boiler specification. Contact your local Cleaver-Brooks authorized representative for information on special insurance requirements, special code requirements, optional equipment, or general assistance in completing the specification.

PART 1 
GENERAL

CBL Steam Boiler (900-1800 hp, Steam 15-250 psig)

1.1 
Boiler Characteristics (Steam)
A.
The Steam Boiler shall be Cleaver-Brooks Fuel Series _____ (100, 200, 400, 600, 700), _____ hp designed for _____ psig (15, 150, 200, or 250 psig steam). The maximum operating pressure shall be _____ psig and the minimum operating pressure shall be _____ psig.

B. 
The boiler shall have a maximum output of _____ Btu/hr, or _____ horsepower when fired with CS12-48 _____ oil and/or natural gas, _____ Btu/cu-ft. Electrical power available shall be _____ Volt _____ Phase _____ Cycle.

PART 2 
PRODUCTS

2.1 
General Boiler Design
A.
The boiler shall be a three pass or four pass horizontal firetube updraft boiler with _____ square feet of heating surface per rated boiler horsepower. It shall be mounted on a heavy steel frame with integral forced draft burner and burner controls.

1. 
The boiler shall be completely preassembled and fire tested at the factory. The unit shall be ready for immediate mounting on floor or simple foundation and ready for attachment of water, fuel, electrical, vent, and blowdown connections.

2. 
The boiler shall be built to comply with the following insurance and codes __________ (Factory Mutual, Industrial Risk Insurance, ASME, NFPA 8501).

B. 
Boiler Shell (Steam)

1. 
The boiler shell must be constructed in accordance with ASME Boiler Code and must receive authorized boiler inspection prior to shipment. A copy of the inspection report shall be furnished to the purchaser.

2. 
The boiler shall be furnished with a manhole and handholes to facilitate boiler inspection and cleaning. Two lifting lugs must be located on top of the boiler.

3. 
The front door shall be davited and the rear door shall be davited. Doors are to be sealed with fiberglass tadpole gaskets and fastened tightly using heavy capscrews that thread into replaceable brass nuts.

4. 
The boiler tubes shall not include turbulators, swirlers, or other add-on appurtenances.

5. 
The rear door shall be insulated with a blanket material with a steel covering to give the surface a hard durable finish.

6. 
The exhaust gas vent shall be located at the front or rear of the boiler and be capable of supporting 2000 lbs. The boiler vent shall contain a stack thermometer.

7. 
Observation ports for the inspection flame conditions shall be provided at each end of the boiler.

8. 
The boiler insulation shall consist of 2 inch blanket under a sectional pre-formed sheet metal lagging. The insulation must be readily removable and capable of being reinstalled, if required.

9. 
The entire boiler base frame and other components shall be factory-painted before shipment, using a hard-finish enamel coating.

10.
The boiler shall contain a chemical feed connection.

2.2 
Steam Boiler Trim
A.
Water Column
A water column shall be located on the right-hand side of the boiler complete with gauge glass set, and water column blowdown valves.

1. 
Modulating feedwater Control

The boiler modulating feedwater control and valve shall be included to automatically maintain the boiler water level within normal limits.

2. 
Low Water Cutoff

The low water cutoff shall be included as an integral part of the boiler feedwater control and wired into the burner control circuit to prevent burner operation if the boiler water level falls below a safe level.

B. 
Auxiliary Low Water Cut-off
Auxiliary low water cut-off shall be included, piped to the vessel, and wired to the burner control circuit. A manual reset device shall be used on this control.

C.
Steam Pressure Gauge
The steam pressure gauge shall be located at the front of the boiler and include cock and test connection.

D.
Safety Valves
Safety valves of a type and size to comply with ASME Code requirements shall be shipped loose.

E. 
Steam Pressure Controls
The steam pressure control to regulate burner operation shall be mounted near the water column. Controls shall be a high limit (manual reset), operating limit (auto reset), and firing rate control.

2.3 
Burner and Controls 
A.
Mode of Operation
1.
Burner operation shall be full modulation principle. The burner shall always return to low fire position for ignition.

2.
A low fire hold temperature control is mounted and wired on the boiler.
B.
Blower

1. 
All air for combustion shall be supplied by a forced draft blower mounted on the burner, to eliminate vibration and reduce noise level.

2. 
Maximum sound level of the boiler/burner package shall not exceed _____ dbA (when measured in accordance with ABMA Sound Test Standards).

3. 
The impeller shall be fabricated aluminum with radial blade, carefully balanced, and directly connected to the blower motor shaft.

C.
Combustion Air Control
Combustion air damper and cam-operated fuel metering valve shall be operated by a single damper control motor that regulates the flame according to load demand. Potentiometer type position controls shall be provided to regulate operation of the damper control motor.

2.4 
Fuel Specification and Piping
Select one of the following fuel types:

· Fuel series 700 - Gas-fired.

· Fuel series 100 - Light oil (No. 2) fired.

· Fuel series 200 - Light oil or gas-fired.

· Fuel series 600 - No. 6 oil-fired.

•
Fuel series 400 - No. 6 oil or gas-fired.

A.
Fuel Series 700 - Gas-Fired

1. 
Burner Type - The burner shall be mounted at the front of the boiler and of high radiant multi-port type gas entry. The burner shall be approved for operation on natural gas fuel.

2. 
Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).

3. 
Gas Burner Piping - Gas burner piping on all units shall include a gas pressure regulator, a primary gas shutoff valve, motor operated with proof of closure switch and plugged leakage test connection. The main gas valves shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve, plus an additional plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves.

4. 
Burner Turndown: Turndown range shall be 8:1 when firing natural gas on standard burners with uncontrolled emissions (100 ppm NOx). Consult Cleaver-Brooks representative regarding turndown capability for low NOx burners 30 ppm and less.

B. 
Fuel Series 100 - Light Oil-Fired

1. 
Burner Type - The burner shall be mounted at the front of the boiler, and shall be a low pressure air atomizing type approved for operation with CS12-48, Commercial No. 2 oil.

2. 
Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).

3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank, shall be provided.

4. 
Oil Burner Piping

a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted on the unit.

5. 
Low Pressure Air Atomizing: Separate air compressor module, “shipped loose” with burner mounted low atomizing air pressure switch.

6. 
Turndown range shall be 6:1 when firing No. 2 oil on standard burners with uncontrolled emissions. Consult Cleaver-Brooks representative regarding turndown capability for low NOx burners.

C.
Fuel Series 200 - Light Oil or Gas-Fired

1. 
Burner Type - The burner shall be mounted at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 Oil or natural gas.

2. 
Gas Pilot - The gas pilot shall be premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and pressure gauge and one (1) plugged leakage test connection (Canada only).

3. 
Oil Burner

a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped loose, shall be provided, to be installed in a location favorable to the oil storage tank.

b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit.

c. 
Low pressure Air Atomizing - Separate air compressor module, “shipped loose” with burner-mounted low-atomizing air pressure switch.

d. 
Burner Turndown - Turndown range shall be 6:1 when firing No. 2 oil on standard burners with uncontrolled emissions. Consult Cleaver-Brooks representative regarding turndown capability for low NOx burners.

4. 
Gas Burner

a. 
Gas Burner Piping - Gas burner piping on all units shall include a gas pressure regulator, and a primary gas shutoff valve, motor-operated with proof-of-closure switch and plugged leakage test connection. The main gas valves shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve, plus and additional plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves.

b. 
Burner Turndown - Turndown range shall be 8:1 when firing natural gas on standard burners with uncontrolled emissions (100 ppm NOx). Consult Cleaver-Brooks representative regarding turndown capability for low NOx burners 30 ppm and less.

D.
Fuel Series 600 - No. 6 Oil-Fired

1. 
Burner Type - The burner shall be mounted at the front of the boiler and low pressure air atomizing type approved for operation with CS12-48, Commercial No. 6 Oil.

2. 
Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and pressure gauge and one (1) plugged leakage test (Canada only).

3. 
Oil Pump - An oil pump set with a capacity of approximately twice the maximum burning rate shall be included.

•
The motor driven pump set, shipped loose, to be installed in a location favorable to the oil storage tank shall be provided.

4. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges all integrally mounted on the unit.

5. 
Low Pressure Air-Atomizing - Separate air compressor module, “shipped loose” with the burner-mounted low-atomizing air pressure switch.

6. 
Oil Preheat
The oil shall be preheated by a steam heater and electric heater, each with thermostatic control. Both heaters shall be installed in a single compact shell; mounted, piped, and wired. The thermostatic controls shall be set to cut-out the electric heater when steam is available.

7. 
Burner Turndown - Turndown range will be 4:1 when firing No. 6 oil on standard burners with uncontrolled emissions. Consult Cleaver-Brooks representative regarding turndown capability for low NOx burners.

E. 
Fuel Series 400 - No. 6 Oil or Gas-Fired

1. 
Burner Type - The burner shall be mounted at the front the boiler and shall be a combination of the low pressure atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 6 oil or natural gas.

2. 
Gas Pilot - The gas pilot shall be a premix type with automatic electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual shut-off valve, solenoid valve, pressure regulator and pressure gauge, and one (1) plugged leakage test connection. (Canada only.)

3. 
Oil Burner

a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor driven pump set, shipped loose, shall be provided to be installed in a location favorable to the oil storage tank.

b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted on the unit.

c. 
Low Pressure Air-Atomizing: Separate air compressor module “shipped loose” with burner mounted low atomizing air pressure switch.

d. 
Oil Preheat - The oil shall be preheated by a steam heater and electric heater, each with thermostatic control. Both heaters shall be installed in a single compact shell mounted, piped, and wired. The thermostatic controls shall be sent to cut-out the electric heater when steam is available.

e. 
Burner Turndown - Turndown range will be 4:1 when firing No. 6 oil on standard burners with uncontrolled emissions. Consult Cleaver-Brooks representative regarding turndown capability for low NOx burners.

f.
Gas Burner

1) 
Gas Burner Piping - Gas burner piping on all units shall include a gas pressure regulator, and a primary gas shutoff valve, motor-operated with proof-of-closure switch and plugged leakage test connection. The main gas valves shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as means for a tightness check of the primary shutoff valve. An additional plug cock shall be furnished at entrance to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve, plus an additional plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves.

2) 
Burner Turndown - Turndown range shall be 6:1 when firing natural gas on standard burners with uncontrolled emissions (100 ppm NOx). Consult Cleaver- Brooks representative regarding turndown capability for low NOx burners 30 ppm and less.

2.5 
Boiler Flame Safeguard Controller and Control Panel 
A.
CB100E Flame Safeguard

1. 
Each boiler shall be factory-equipped with flame safeguard controller providing technology and functions equal to the Cleaver-Brooks Model CB100E.
Flame safeguard shall be a Cleaver-Brooks Model CB 100E microprocessor-based control to monitor all critical boiler and burner interlocks, control and supervise burner light-off sequence, and initiate an orderly safety procedure in the event of interlock or flame failure. The system shall provide status, fault history, and diagnostic information by means of a BACKLIT LCD display. The system shall be approved by UL, FM, and CSA, and shall be acceptable by IRI.

B. 
Control Panel
A factory prewired control panel shall be supplied with the boiler/burner package. Panel may be mounted on the burner or boiler.

1. 
The panel will have a NEMA 1A rating and contain the flame safeguard controller, burner motor starter, air compressor motor starter, oil-metering pump motor starter, control circuit transformer and fuses, selector switches, indicating lights and terminal strips. Lights shall indicate load demand, flame failure, low water, and fuel valve open.

2. 
The panel shall contain over-current protection for the burner motor, air compressor motor, and oil metering pump.

2.6 
Efficiency Guarantee
A.
The boiler must be guaranteed to operate at a minimum fuel-to-steam efficiency of _____ percent at 100 percent of rating when burning natural gas and _____ fuel-to-steam efficiency at 100% firing rate when burning oil (Contact your local Cleaver-Brooks authorized representative for efficiency details).

PART 3 
EXECUTION

3.1 
Warranty
A. 
All equipment is to be guaranteed against defects in materials and/or workmanship for a period of 12 months from date of start-up, or 18 months from date of shipment; whichever comes first.

3.2 
Shop Tests
A.
The packaged boiler must receive factory tests to check the construction, controls, and operation of the unit. All tests may be witnessed by the purchaser, if desired.

B. 
Start-up Service

1. 
After boiler installation is completed, the manufacturer shall provide the services of a field representative for starting the unit and training the operator at no additional costs.

a. 
A factory-approved and authorized start-up report shall be submitted to the customer/user at the time of start-up.






Section (ie. B9)-Page #
Rev. date (ie. Rev. 11-10)
Section A5-1
Rev. 03-08

