[image: image1.png]CleaverBrooks' b



[image: image2.png]CleaverBrooks' b





Model 5 Boilers
Steam Specifications
[image: image3.png]CleaverBrooks' b



Boiler Capacity . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . B3-32
Boiler Description . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . B3-32
Soot Cleaning  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . B3-33
Boiler Connections . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . B3-33
Boiler Trim/Controls . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . B3-33
Low Water Volume Design (LWV), 150 Psig  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . B3-34
Low Water Volume Design (LWV), 15 Psig  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . B3-34
Burner . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . B3-34
Gas Fired Burner . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . B3-35
Oil Fired Burner  . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . B3-36
Gas-Oil Fired Burner . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . B3-37
Burner and Flame Failure Controller . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . B3-38
Burner Control Panel . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . B3-38
SAMPLE SPECIFICATIONS
The following sample specifications are provided by Cleaver-Brooks to assist you in specifying your customer’s specific needs and application.

[image: image4.png]CleaverBrooks' b



PART 1 
GENERAL 
1.1 
BOILER CAPACITY

A.
The steam boiler shall be a Cleaver-Brooks Model 5, Series (100,
200, 700) rated at  
lbs/hr or  
boiler horsepower designed for (15, 150, 250, 350 or 500) psig steam. The maximum boiler operating pressure will be  

psig. (Series

100 is a No.2 oil fired burner; Series 200 is a gas or No.2 oil fired burner; Series 700 is a straight gas burner).

B.
The boiler shall have a maximum output of  
Btu/hr or

 
boiler horsepower when fired with (No.2 oil) or (natural gas

@  
Btu/cu-ft). The boiler shall develop  
lbs/hr when operating at  
psig with feedwater temperature at

 
o F.  The boiler safety relief valve(s) shall be set at  

psig.

C.
Electrical power to the boiler shall be  
volts,  
phase,

 
Hz. All electrical service connections shall be made to an electrical entrance box mounted on the right hand side of the boiler.

PART 2 
PRODUCTS
2.1 
BOILER DESCRIPTION

A.
The boiler shall be an all steel membrane wall watertube design with 3-pass gas travel. It shall be mounted on a heavy duty steel frame with an integral forced draft burner and burner controls. The complete package, boiler-burner unit, shall be certified, tested, and labeled by CSA (Canadian Standard Association). The package shall be completely assembled and receive a factory fire test prior to shipment.

B.
The boiler shell must be constructed and hydrostatically tested in accordance with the A.S.M.E. Boiler and Pressure Vessel Code Section I or IV and receive an authorized boiler inspection. A copy of the inspection report shall be furnished to the purchaser.

C.
Two downcomers shall be located at the rear of the boiler and totally insulated from the generating tubes. The downcomers shall be 2-1/
2" OD for 35 and 47 hp; 3" OD for 59 to 83 hp, and 4" OD for 95 hp and greater. Material shall be SA-178A. The 2-1/2" and 3" downcomers shall have 0.105" wall while the 4" downcomers shall

have 0.135" wall.  The generating tubes shall be 2" OD, SA-178

Grade A with 0.095" wall thickness.

D.
The upper drum shall be 20" OD Schedule 20, SA-53-B seamless pipe with 0.375" wall.  The lower drum shall be 6" nominal pipe size, SA-53-B seamless pipe with 0.312" wall up through 150 psig design.

E.
Two lifting eyes shall be located on the top centerline of the upper drum.

F.
Refractory shall be limited to the furnace floor, lower drum, burner throat tile, and the formed rear furnace access door. High temperature insulation shall be installed on the front water wall of the furnace.

G.
Observation ports shall be provided at each end of the boiler for visual inspection of the pilot and main flame conditions.

[image: image5.png]CleaverBrooks' b



H. 
The exhaust gas vent shall be located at the top rear centerline of the boiler. A stack thermometer shall be shipped loose for field installation by the installing contractor into the stack.

I. 
Inspection openings shall be provided in the convection area.

J.
The lower drum shall include capped plugs in the front and rear drum heads, and a handhole shall be provided in the rear upper drum head for waterside inspection

K.
The vessel shall be insulated with a minimum of 2" fiber glass blanket. This insulation shall be covered with a sheet metal jacket. The jacket and insulation shall be arranged for easy removal and reinstallation if required.

L.
The entire boiler jacket, base frame, and other components shall be factory painted using hard finish enamel.

2.2 
SOOT CLEANING

A.
Soot washer lances shall be provided in the upper convection area of the boiler, measuring the full length of the pressure vessel. Each lance assembly shall be capable of rotating 360 degrees. This shall ensure complete washing of the convection zone while the boiler is operating in the low fire mode.

B.
Soot washer drain troughs shall be provided at the bottom of the boiler. These shall be furnished for each convection side running the full length of the boiler with 2" drain connections at the bottom rear. Inspection/cleanout openings for each trough shall be located at the front of the boiler.

2.3 
BOILER CONNECTIONS

A.
The steam nozzle shall be located on the top centerline of the upper drum and sized for steam velocity not to exceed 5000 fpm.

B.
A feedwater tapping and an integral feedwater distribution pipe shall be located in the upper drum. This distribution pipe shall blend the feedwater with the boiler water.

C.
A ¾" surface blowoff tapping shall be provided in the rear head of the upper drum.

D.
For blowdown or boiler drain, a tapping shall be provided in the bottom of the lower drum near the front of the boiler.

2.4 
BOILER TRIM/CONTROLS

A.
The primary water column shall be located on the left side of the boiler when facing the burner. It shall be piped with union connections for easy removal and include a full size column blowdown valve. A gauge glass with gauge glass valves shall be mounted to the water column.

B.
A primary low water cutoff switch shall be an integral part of the water column and shall be wired into the burner control circuit to prevent burner operation in the event of an unsafe water level condition.

C.
To maintain proper and safe water level within the boiler, an integral feed pump control switch shall be included within the primary water column. This switch may be wired to a control relay for pump on/off operation or wired to control a solenoid water make-up valve.

[image: image6.png]CleaverBrooks' b



Section B2-33
Rev. 03-08
[image: image7.png]CleaverBrooks' b



D.
A secondary low water cutoff control of the manual reset type shall be provided on the right hand side of the boiler, when facing the burner. This control shall include a switch wired into the burner circuit to prevent burner operation in the event that the primary low water control did not function properly during an unsafe water level condition. A control blowdown valve shall be included for maintenance and periodic testing of the level device.

E.
For visual indication of the internal boiler pressure, a steam pressure gauge shall be mounted near the water column and shall include an inspector's test cock and test connection point.

F.
For burner operation, a minimum of three controls shall be provided: one auto reset type for burner start and stop control, one for burner firing rate (modulation on gas or low high low on oil), and one manual reset type for burner shutdown in the event of excessive steam pressure within the boiler.

G.
In compliance with the A.S.M.E. Code, a Code rated safety relief valve(s) shall be provided. This valve(s) may be shipped loose to prevent any damage during shipment.

2.5 
LOW WATER VOLUME DESIGN (LWV), 150 PSIG

For applications requiring the use of a low water volume vessel, the following trim, controls and design shall be provided:

A.
The primary water column shall be located on the left side of the boiler when facing the burner, and shall be a McDonnell-Miller

#193-7 or approved equal. It shall be piped with union connections for easy removal and include a full size column blowdown valve. A gauge glass with gauge glass valves shall be mounted to the water column.

B.
The primary water level control and water level cut-off settings shall be installed at a level that limits the total water content within the boiler to 75 U.S. Gallons (283.9 liters) or less at full operating capacity.

C.
Feedwater into the boiler shall be controlled by means of an electric proportional feedwater valve, Worchester or approved equal, complete with stop valve, check valve, and 3-valve by-pass.

D.
Controls shall be provided to comply with "Guarded Plant" status requirements.

E.
The upper and lower drums shall be properly insulated to prevent heat transfer onto these surfaces during combustion.

2.6 
LOW WATER VOLUME DESIGN (LWV), 15 PSIG
For applications requiring the use of a low water volume vessel, the following trim, controls and design shall be provided:

A.
Controls shall be provided to comply with "Guarded Plant" status requirements.

B.
The upper and lower drums shall be properly insulated to prevent heat transfer onto these surfaces during combustion.

[image: image8.png]CleaverBrooks' b



2.7 
BURNER

A.
Models 1500 - 6000; all air for combustion shall be supplied by a

Section B2-34
Rev. 03-08
forced draft blower mounted in the front head (wind box) above the burner, to minimize vibration and reduce noise emissions. The impeller shall be an enclosed centrifugal fan type, properly balanced and direct connected to the motor shaft. Sound level shall not exceed 80 dBA measured 3 feet in front of the burner.

B.
Models 7500 - 8000; all air for combustion shall be supplied by a forced draft blower mounted within the fan housing of the externally mounted burner. The burner shall be a CB Profire Series V. The fan shall be a squirrel cage design, properly balanced and direct connected to the motor. Sound level shall not exceed 85 dBA measured 3 feet in front of the burner.

C.
When firing gas, the burner shall operate on the full modulation mode and shall be positioned at the low position for the ignition sequence, and shall remain in the low fire position during ignition and until main flame has been proven.

D.
For oil operation, the burner shall operate on the low-high-low principle and shall be positioned at the low position for the ignition sequence, and shall remain in the low fire position during ignition and until main flame has been proven.

2.8 
GAS FIRED BURNER

A.
The burner shall be a high radiant multi-port type approved for operation on natural gas.

B.
Automatic electric ignition of the premix gas pilot shall be furnished.

An ultra violet (UV) flame detector shall monitor the pilot, preventing the primary fuel valve from opening until the pilot flame has been established. The gas pilot assembly shall include a pilot solenoid shutoff valve, pilot regulator, and manual shutoff cock.

C.
A single damper motor shall control the combustion air inlet damper and the fuel input control valve (butterfly type) via linkage connections. The damper motor shall modulate the burner in accordance with system demand, responding to the boiler mounted modulating pressure control.

D.
Gas burner piping shall include a primary safety shutoff valve, controlled by the burner flame safeguard control to start or stop the burner. The valve shall close automatically in the event of a power failure, excess steam pressure, low or high gas pressure, or a low water condition.

E.
A main gas pressure regulator shall be piped in the gas train to regulate the incoming pressure for proper burner operating pressure including an upstream manual shutoff valve.

F.
For tightness checking of the primary shutoff valve, a plugged leakage test connection and a lubricated plug cock shall be provided.

G.
The primary shutoff valve shall be of the motorized type.

H. 
For sizes 6000 - 8000, a second motorized gas valve shall be provided and piped in series with the primary shutoff valve.

I. 
Low and High gas pressure switches of the manual reset type shall be mounted and wired to prevent burner operation if gas pressure is above or below the settings of these switches.

Section B2-35
Rev. 03-08
J.
To prove proper air is available for pre purge and combustion, a combustion air proving switch shall be provided.

2.9 
OIL FIRED BURNER

A.
The burner shall be a pressure atomizing type approved for operation with commercial grade No. 2 fuel oil.
B.
For 1500 through 6000 units,

1. 
Automatic electric spark ignition for the low fire oil supply shall be provided with a 10,000 volt ignition transformer and heavy duty electrodes. The ignition period shall be monitored with an electronic scanner of the UV principle to confirm the presence of the low fire oil flame.

2. 
A single damper motor shall control the combustion air inlet damper and the fuel input control valves via linkage connections. The damper motor shall operate the burner in accordance with system demand, responding to the boiler mounted low high low pressure control.

3. 
For fuel input control, 4 solenoid type fuel oil valves shall be piped and wired onto the front head of the boiler. Two valves shall be used for low fire ignition and the other two for high fire operation.

4. 
The fuel oil system shall include supply and return tubing to an oil terminal block, oil pressure gauge, and shutoff cock.

5. 
An oil pump shall be provided and shall be integral with the burner. The pump shall include a built-in pressure relief valve and self cleaning strainer. Operation of the pump shall be via belt connection to the fan motor.

C.
For 7500 - 8000 units, automatic electric ignition of the premix gas pilot shall be furnished. An ultra violet (UV) flame detector shall monitor the pilot, preventing the primary fuel valve from opening until the pilot flame has been established. The gas pilot assembly shall include a pilot solenoid shutoff valve, pilot regulator, and manual shutoff cock.

1. 

A single damper motor shall control the combustion air inlet damper and the fuel input control valve via linkage connections. The damper motor shall modulate the burner in accordance with system demand, responding to the boiler mounted modulating pressure control.

2. 
For fuel input control, metering type fuel oil valve shall be piped and onto the burner housing. Two solenoid valves shall be used for safety shutoff.

3. 
The fuel oil system shall include supply and return tubing to an oil terminal block, oil pressure gauge, low oil pressure interlock, and shutoff cock.

4. 
An oil pump shall be provided and shall be shipped loose with the burner. The pump shall include a built-in pressure relief valve and self cleaning strainer. Operation of the pump shall be via oil pump starter mounted and wired in the burner control panel.

Section B2-36
Rev. 03-08
2.10 

GAS-OIL FIRED BURNER A.
A. General
1. 
The burner shall be a high radiant multi-port type approved for operation on natural gas and shall be a pressure atomizing type approved for operation with commercial grade No. 2 fuel oil.
2. 
Automatic electric ignition of the premix gas pilot shall be furnished. An ultra violet (UV) flame detector shall monitor the pilot, preventing the primary fuel valve from opening until the pilot flame has been established. The gas pilot assembly shall include a pilot solenoid shutoff valve, pilot regulator, and manual shutoff cock.

3. 
A single damper motor shall control the combustion air inlet damper and the fuel input control valve via linkage connections. The damper motor shall regulate the burner in accordance with system demand, responding to the boiler mounted pressure control.

4. 
To prove proper air is available for pre purge and combustion, a combustion air proving switch shall be provided.

B.
Gas System
1. 
Gas burner piping shall include a primary safety shutoff valve, controlled by the burner flame safeguard control to start or stop the burner. The valve shall close automatically in the event of a power failure, excess steam pressure, low or high gas pressure, or a low water condition.

2. 
A main gas pressure regulator shall be piped in the gas train to regulate the incoming pressure for proper burner operating pressure including an upstream manual shutoff valve.

3. 
For tightness checking of the primary shutoff valve, a plugged leakage test connection and a lubricated plug cock shall be provided.

4. 
The primary shutoff valve shall be of the motorized type.

5. 
For sizes 6000 - 8000, a second motorized gas valve shall be provided and piped in series with the primary shutoff valve.

6. 
Low and High gas pressure switches of the manual reset type shall be mounted and wired to prevent burner operation if gas pressure is above or below the settings of these switches.

C.
Oil System
1. 
For 1500 through 6000 units,

a.
For fuel input control, 4 solenoid type fuel oil valves shall be piped and wired onto the front head of the boiler. Two valves shall be used for low fire ignition and the other two for high fire operation.

b.
The fuel oil system shall include supply and return tubing to an oil terminal block, oil pressure gauge, and shutoff cock.

c.
An oil pump shall be provided and shall be integral with the burner. The pump shall include a built-in pressure relief valve and self cleaning strainer. Operation of the pump shall be via belt connection to the fan motor.

Section B2-37
Rev. 03-08
2. 
For 7500 - 8000 units,
a.
For fuel input control, metering type fuel oil valve shall be piped and onto the burner housing. Two solenoid valves shall be used for safety shutoff.

b.
The fuel oil system shall include supply and return tubing to an oil terminal block, oil pressure gauge, low oil pressure interlock, and shutoff cock.

c.
An oil pump shall be provided and shall be shipped loose with the burner. The pump shall include a built-in pressure relief valve and self cleaning strainer. Operation of the pump shall be via oil pump starter mounted and wired in the burner control panel.

2.11 
BURNER AND FLAME FAILURE CONTROLLER
A third party listed and approved safeguard control shall be provided to control ignition, starting and stopping the burner, and provide pre-combustion and post combustion air purge.  The control shall stop and prevent burner operation in the event of ignition, pilot, or main flame failures. Trial for ignition shall be limited to

10 seconds.
A.
The flame safeguard control shall be a microprocessor based burner management control system, designed to provide proper burner sequencing, ignition, and flame monitoring protection.

B.
Through SMART LED's, the control shall provide current operating status and lockout information in the event of a safety shutdown.

C.
A separate preconfigured program module shall plug in to the microprocessor control.

D.
For trouble shooting and retrieving history, a VFD format display shall be mounted onto the control. This alpha numeric display shall provide 2 lines by 16 characters per line display of operating conditions, fault conditions, flame signal strength, and burner run history.

E.
In addition to the VFD display, LED Indicator Lights shall be provided integral with the control for Fan, Open Damper, Close Damper, Auto Operation, and Ignition.

F.
The control shall be a CB120E or equal.
2.12 
BURNER CONTROL PANEL
A.
The control panel shall be mounted at the front of the boiler on the burner fan housing (windbox) and conveniently located for the operator. It shall be mounted within a NEMA 1A type enclosure and include a key lock.

B.
Factory mounted and wired components and controls shall include the following:

1. 
Fan Motor Starter
2. 
Fan Motor Fuses
3. 
Control Circuit Transformer with fuses

4. 
Oil Pump Starter (size 7500 - 8000 units) firing oil.
5. 
Terminals for wiring connections

Section B2-38
Rev. 03-08
6. 
Flame Safeguard Control
7. 
Burner On/Off Switch
8. 
Manual Damper Positioning Switch

9. 
Indicating lights for low water, flame failure, load demand, and fuel valve on.

C.
All electrical equipment shall be in conformity with CSA. Oil, heat, and moisture resistant wire shall be used and number coded relative to the wiring diagram.

Section B2-39
Rev. 03-08



�








�








�








�








�








�








�













