[image: image1.png]CleaverBrooks’ b



Model (ie. Model CFV)


Group (ie. Commercial Boilers

HAWK MASTER PANEL 

Lead/Lag for Up to Eight Boilers System

Sample Specifications
HAWK — Lead/lag for up to
Eight Boilers System

PART 1 
GENERAL
1.1 
GENERAL

A.
Lead/Lag Start with either Lead/Lag or Unison Modulation. 
B.
Boilers’ Start and Stop

1. 
Steam pressure, or hot water temperature on hot water systems, is compared with the setpoint and controller’s processor executes PID algorithm. Lead boiler is commanded to come on-line first. Lag boiler #1 is commanded to come on- line when a firing rate signal for the lead boiler reaches lag boiler start point. Lag boiler #1 is commanded to stop when a firing rate signal for the lead boiler reaches lag boiler stop point.

2. 
Lag boiler #2 is commanded to come on-line when a firing rate signal for the lag boiler #1 reaches lag boiler #2 start point. Lag boiler #2 is commanded to stop when a firing rate signal for the lag boiler #1 reaches lag boiler #2 stop point.

3. 
Subsequent boilers operate in a similar fashion. 
C.
Lead/Lag Modulation

1. 
Lag boiler #1 starts modulation after lead boiler reaches maximum firing rate (or firing rate selected by the operator).

2. 
Lag boiler #2 starts modulation after lag boiler #1 reaches maximum firing rate (or firing rate selected by the operator).

3. 
Subsequent boilers operate in a similar fashion.

D.
Unison Modulation - Firing rates for all boilers are equal.

E. 
Hot Standby - System shall have a provision for keeping lag boilers in hot standby. Standby routine shall be based on a water temperature signal.

F. 
Firing Sequence Selection - Sequence in which boilers come on-line shall be selected via HMI. Adequate check shall be provided that does not allow improper sequence selection.

G.
Automatic Rotation of the Boilers - System shall be provided with a sequence to automatically rotate sequence in which the boilers are fired. Rotation shall be based on the elapsed time.

1.2 
HMI (HUMAN MACHINE INTERFACE)

A.
Master panel shall include HMI for display and selection of the following parameters:

B. 
Display

1. 
Available boilers

2. 
Number of boilers required

3. 
Selected sequence of firing

4. 
Control output to each boiler

5. 
Header steam pressure or water temperature on hot water systems

6. 
Setpoint

7. 
Elapsed time from last rotation

C.
Selection

1. 
Number of boilers

2. 
Sequence of firing

3. 
Automatic or manual rotation

4. 
Individual boiler start and stop points with timers

5. 
Setpoint

6. 
Proportional, integral and derivative gains for control algorithm

1.3 
APPLICATION AND SYSTEM REQUIREMENTS

A.
This option is applicable to full modulation burners utilizing the HAWK advanced boiler control system and modulating controls.

B. 
Logic for Lead/Lag control shall reside in the Master Control Panel. Communication between the Master Panel and the individual Boiler Control Panels shall be via Ethernet communication or hard wiring.
Section (ie. B9)-Page #
Rev. date (ie. Rev. 11-10)
Section D-1
Rev. 09-09

