[image: image1.png]


[image: image2.png]





Sample Specifications Steam
Model CBEX Elite 100-800 HP
GENERAL
Boiler Characteristics  (Steam)  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 22
PRODUCTS
General Boiler Design  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 22
Steam Boiler Trim
- - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 23
Burner   - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 23
Fuel Specification And Piping  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 24
60 PPM- - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 24
30 PPM- - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 29
9 PPM  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 35
7 PPM  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 41
Boiler Controls And Control Panel   - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 47
Flue Gas Heat Recovery (Optional Selection)  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 47
Efficiency Guarantee   - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 47
EXECUTION
Warranty - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 47
Shop Tests   - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 47
SAMPLE SPECIFICATIONS
The following sample  specifications  are provided by Cleaver-Brooks to assist  you in meeting  your customer's specific needs and application.
The Sample  Specifications  are  typically utilized as  the  base  template  for the  complete  boiler specification. Contact your local Cleaver-Brooks authorized representative  for information on special insurance  requirements, special code requirements, optional equipment, or general assistance in completing the specification.
PART 1 
GENERAL
CBEX Steam Boiler 100-800 HP
1.1 
BOILER CHARACTERISTICS (STEAM)
A.
The Steam Boiler shall be Cleaver-Brooks Fuel Series  
(100, 200, 700),  
hp designed for  

psig (150, 200, or 250  psig steam).  The maximum operating pressure shall be  
psig and the minimum operating pressure shall be  
psig (note - minimum allowable operating pressure on the CBEX is 50 psig).
B. 
The boiler shall have a maximum output of  

Btu/hr, or  
horsepower when fired with CS12-48 #2 oil and/or natural gas,  
Btu/cu-ft. Electrical power available shall be
 
Volt  
Phase  
Cycle.
PART 2 
PRODUCTS
2.1 
GENERAL BOILER DESIGN
A.
Design shall be optimized using CFD modeling verifiable by manufacturer.  The boiler shall be a multipass  pass horizontal firetube updraft boiler with using extended heating surface optimized to reduce boiler foot print. Boiler shall be mounted  on a heavy steel frame with integral forced draft burner and burner controls.
1. 
The boiler shall be completely preassembled and fire tested  at the factory. The unit shall be ready for immediate mounting on floor or simple foundation and ready for attachment of water, fuel, electrical, vent, and blowdown connections.
2. 
The boiler shall be built to comply with the following insurance  and codes    (Factory
Mutual, XL GAP, ASME, NFPA 8501).
B. 
Boiler Shell (Steam)
1. 
The boiler shell must be constructed  in accordance  with ASME Boiler Code and must receive authorized boiler inspection prior to shipment. A copy of the inspection report shall be furnished to the purchaser.
2. 
The boiler shall be furnished with a manhole  and handholes  to facilitate boiler inspection and cleaning. Two lifting lugs must be located on top of the boiler.
3. 
The front smokebox doors shall be davited and sealed with superwool insulation and fastened tightly using locking lugs on steel studs.
4. 
The rear head shall be fitted with an access  plug for rear fireside inspection.
5. 
The boiler tubes shall not include turbulators,  swirlers, or other add-on appurtenances.
6. 
The exhaust gas vent shall be located at the front of the boiler and be capable  of supporting 2000 lbs. The boiler vent shall contain a stack thermometer.
7. 
Observation ports for the inspection of flame conditions shall be provided at each end of the boiler.
8. 
The boiler insulation shall consist of 2 inch blanket under a sectional pre-formed sheet metal lagging. The insulation must be readily removable and capable of being reinstalled if required.
9. 
The entire boiler base frame and other components  shall be factory painted  before shipment, using a hard-finish enamel coating.
10.   The boiler shall contain a chemical feed connection.
2.2 
STEAM BOILER TRIM
A.
Water Column/low Water Cutoff And Water Level Control System shall be a CB LEVEL MASTER water level control system and shall comprise a microprocessor-based electronic controller, a non-contact,  non-wearing,  continuously reading absolute level sensor, and pressure chamber. The control system shall be designed as follows: The electronic controller shall be mounted  in the common control panel and operate in ambient  temperatures from 32 degrees F to 125 degrees F. The pressure chamber  shall be boiler mounted and operate to pressures  of 250  PSIG and the level sensor shall operate to pressures  of 250  PSIG and temperatures to 400  degrees F. The pressure-containing components  shall be constructed  in accordance  with ASME Code. A shielded,  four conductor cable with ground shall be run in metal conduit between the level sensor and the controller. Supply power shall be 115VAC-1 phase- 60 Hz. All wiring shall be in compliance with the National Electrical Code.
The pressure chamber  shall have a sight glass mounted  on the side. The level sensor shall have an  accuracy  of .01"  or greater.  The electronic  controller shall  have  level and  error indicating lights, alphanumeric display for messaging,  reset/ menu switch and the following features:
a. 
Continuous Level Indication b. 
Low Water Cutoff & Alarm c.
High Water Alarm
d. 
Low & High Water Warning
e. 
Full Modulating Control of Modulating Feedwater  Control Valve f.
Continuous Monitoring of Float Operation
g. 
Column Blowdown Detection and Reminder h. 
Auto or Manual Reset
i. 
Real Time Clock
j. 
Alarm Annunciation
k. 
Alarm History Files with Time Stamp l. 
Water Column Blowdown Record
m. 
Auxiliary Low Water Cutoff Check n. 
RS 232  Interface
Maximum Contacts Rating 15 amps Resistive Load
B. 
Modulating feedwater Control
The boiler modulating feedwater control and valve shall be included to automatically  maintain the boiler water level within normal limits.
C.
Auxiliary Low Water Cut-off
Auxiliary low water cut-off shall be included, piped to the vessel, and wired to the burner control circuit. A manual  reset device shall be used on this control.
D.
Steam Pressure  Gauge
The steam  pressure gauge shall be located at the front of the boiler and include cock and test connection.
E. 
Safety Valves
Safety valves of a type and size to comply with ASME Code requirements  shall be shipped loose.
F. 
Steam Pressure  Controls
The steam  pressure control to regulate burner operation shall be mounted  near the water column. Controls shall be a high limit (manual reset), operating limit (auto reset), and firing rate control.
2.3 
BURNER
A.
Burner shall incorporate Cleaver Brooks “Lean Burn Technology”.
B. 
Fuel and air ratio/mixture shall be controlled over the entire operating range, allowing for firing at constant  excess air on high turndown burner application.
C.
Burner to be designed specifically for boiler including optimized furnace allowing for low emissions and lean burn combustion.
D.
Mode of Operation
1. 
Burner operation shall be full modulation principle. The burner shall always return to low fire position for ignition.
2. 
A low fire hold temperature control is mounted  and wired on the boiler. E. 
Blower
1. 
Air for combustion  shall be supplied by a forced draft blower incorporated  into the burner design to eliminate vibration and reduce noise level.
2. 
Maximum sound level of the boiler/burner package shall not exceed  
dbA (when measured  in accordance  with ABMA Sound Test Standards).
3. 
The impeller shall be cast aluminum  with radial blade, carefully balanced, and directly connected  to the blower motor shaft.
F. 
Combustion Air Control
Combustion air damper  and fuel metering valve shall be operated  by individual actuators  to regulate the flame according to load demand.
2.4 
FUEL SPECIFICATION AND PIPING
Select one of the following fuel types:
• Fuel series 700  - Gas-fired.
• Fuel series 100  - Light oil (No. 2) fired .
• Fuel series 200  - Light oil or gas-fired.
NOTE: Specification writer to select  between  NOx options of 60  ppm, 30  ppm, 9 ppm or 7 ppm Nox on Natural Gas as required for specific project conditions.
60  PPM Nox Operation Natural Gas
CBEX 100 to 200 Horsepower 60 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 4:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5. 
CO on Natural Gas is 10 ppm at 50,  75 and 100  % of firing and 25 ppm at 25%  firing rate. Excess air is 15%  at 50,  75 and 100% of firing and 30%  at 25%  firing rate.
B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 4:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 4:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 4:1  when firing natural gas.
c. 
CO on Natural Gas is 10 ppm at 50,  75 and 100  % of firing and 25 ppm at 25% firing rate. Excess air is 15%  at 50,  75 and 100% of firing and 30%  at 25%  firing rate.
CBEX 250 and 300 Horsepower 60 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 10:1 when firing natural gas. VSD required to maintain  3% O2 over turndown range.
5. 
CO on Natural Gas is 10 ppm with excess air at 15%  in firing range of 50%  to 100%
increasing to 50 ppm CO at 10:1 turndown.
B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 7:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 7:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of
power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 10:1 with 15%  excess air when firing natural gas. VSD required to maintain  3% O2 over turndown range.
c. 
CO on Natural Gas is 10 ppm at 50%  to 100% firing, increasing to 50 ppm CO at
10:1 turndown
CBEX 350 to 800 Horsepower 60 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 10:1 while holding 15%  excess air across the turndown range. VSD required to hold excess air across firing range on natural gas.
5. 
CO on Natural Gas is 10 ppm with excess air at 15%. B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges,
all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 8:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 8:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 10:1 when firing natural gas with 15% excess air over the turndown range. VSD required to maintain  excess air over turndown range.
c. 
CO on Natural Gas is 10 ppm with excess air at 15%.
30  PPM Nox Operation Natural Gas
CBEX 100 to 200 Horsepower 30 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 4:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5. 
CO on Natural Gas is 25 ppm at 50,  75 and 100  % of firing and 50 ppm at 25%  firing rate. Excess air is 15%  at 50,  75 and 100% of firing and 30%  at 25%  firing rate.
B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 4:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or
natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 4:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 4:1  when firing natural gas.
c. 
CO on Natural Gas is 25 ppm at 50,  75 and 100  % of firing and 50 ppm at 25% firing rate. Excess air is 15%  at 50,  75 and 100% of firing and 30%  at 25%  firing rate.
CBEX 250 and 300 Horsepower 30 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 10:1 when firing natural gas with 15% excess air across the firing range. VSD is required to hold 15%  excess air across the firing range.
5. 
CO on Natural Gas is 10 ppm with excess air at 15%,  from 50%  to 100% firing.CO will increase to 50 ppm at 10:1 turndown.
B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 7:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
b. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
c. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
d. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
e. 
 Burner Turndown - Turndown range shall be 7:1  when firing No. 2 oil. f. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 10:1 when firing natural gas with 15% excess air over the turndown range. VSD required to hold excess air over the turndown range.
c. 
CO on Natural Gas is 10 ppm with excess air at 15%,  from 50% to 100% rating. CO
will increase to 50 ppm at turndown of 10:1.
CBEX 350 to 800 Horsepower 30 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 10:1 while holding 15%  excess air across the turndown range. VSD required to hold excess air across firing range on natural gas.
5. 
CO on Natural Gas is 10 ppm with excess air at 15%. B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low
pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 8:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 8:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located
between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 10:1 while holding 15%  excess air across the turndown range. VSD required to hold excess air across firing range on natural gas.
c. 
CO on Natural Gas is 10 ppm with excess air at 15%.
9 PPM Nox Operation Natural Gas
CBEX 100 to 200 Horsepower 9 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 4:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5. 
CO on Natural Gas is 25 ppm with excess air at 25%. B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 4:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 4:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 4:1  when firing natural gas. c. 
CO on Natural Gas is 25 ppm with excess air at 25%.
CBEX 250 to 400 Horsepower 9 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 5:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5. 
CO on Natural Gas is 25 ppm with excess air at 25%. B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 5:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 5:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 5:1  when firing natural gas. c. 
CO on Natural Gas is 25 ppm with excess air at 25%.
CBEX 500 and 600 Horsepower 9 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 6:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5. 
CO on Natural Gas is 25 ppm with excess air at 25%. B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 6:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 6:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff
valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 6:1  when firing natural gas. c. 
CO on Natural Gas is 25 ppm with excess air at 25%.
CBEX 700 and 800 Horsepower 9 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be  7:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5. 
CO on Natural Gas is 25 ppm with excess air at 25%. B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil
metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 7:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 7:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 7:1  when firing natural gas. c. 
CO on Natural Gas is 25 ppm with excess air at 25%.
7 PPM Nox Operation Natural Gas
CBEX 100 to 200 Horsepower 7 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 3:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5. 
CO on Natural Gas is 50 ppm with excess air at 30%. B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 3:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, b. and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 3:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 3:1  when firing natural gas. c. 
CO on Natural Gas is 50 ppm with excess air at 30%.
CBEX 250 to 500  Horsepower 7 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 4:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5. 
CO on Natural Gas is 50 ppm with excess air at 30%.
B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 4:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 4:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 4:1  when firing natural gas. c. 
CO on Natural Gas is 50 ppm with excess air at 30%.
CBEX 600 to 800 Horsepower 7 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be  5:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5. 
CO on Natural Gas is 50 ppm with excess air at 30%. B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 5:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 5:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 5:1  when firing natural gas. c. 
CO on Natural Gas is 50 ppm with excess air at 30%.
2.5 
BOILER CONTROLS AND CONTROL PANEL
A.
Control/Entrance Panel - A common enclosure shall house the control panel and the entrance panel. Enclosure shall be NEMA 4/12  rated and shall be mounted  at the side of the boiler in a location convenient to the operator. Enclosure shall consist of upper and lower sections divided by a partition with a separate  hinged door for each section. Upper section (low voltage) will house boiler controls including flame safeguard and water level system controller. Lower panel section (high voltage) will house entrance  panel.
B. 
Cleaver Brooks Combustion Control System - Hawk 2000 with parallel positioning with separate actuators  for each fuel and combustion  air shall be used to provide proper fuel air ratio control.
C.
CB780E Flame Safeguard - Each boiler shall be factory equipped  with flame safeguard controller incorporated  into the Hawk control.
Oil, heat  and  moisture  resistant  wire shall be used  and  identified with circuit numbers  corresponding  to the electrical wiring diagram.
Boiler to be supplied with a control circuit transformer and fuse protection for the control circuit.
2.6 
FLUE GAS HEAT RECOVERY (OPTIONAL SELECTION)
A.
Add Cleaver Brooks economizer selection in this area.
B. 
Boiler and economizer to be designed with integral supports  allowing for easy economizer installation on boiler eliminating the requirement  for separate  structure  steel support.
2.7 
EFFICIENCY GUARANTEE
A.
The boiler must be guaranteed to operate at a minimum fuel-to-steam efficiency of  

percent at 100% of rating when burning natural gas and  
fuel-to-steam  efficiency at
100% firing rate when burning oil (Contact your local Cleaver-Brooks authorized representative for efficiency details).
PART 3 
EXECUTION
3.1 
WARRANTY
A.
All equipment  is to be guaranteed against defects in materials  and/or workmanship  for a period of 12 months  from date of start-up,  or 18 months  from date of shipment;  whichever comes first.
3.2 
SHOP TESTS
A.
The packaged  boiler must receive factory tests to check the construction,  controls, and operation of the unit. All tests may be witnessed  by the purchaser, if desired.
B. 
Start-up Service
1. 
After boiler installation is completed,  the manufacturer  shall provide the services of a field representative  for starting the unit and training the operator at no additional costs.
2. 
A factory-approved and authorized start-up report shall be submitted  to the customer/user at the time of start-up.
Sample Specifications Hot Water
Model CBEX Elite 100-800 HP
GENERAL
Boiler Characteristics  (Hot Water)  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 50
PRODUCTS
General Boiler Design  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 50
Hot Water Boiler Trim - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 51
Burner   - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 51
Fuel Specification And Piping  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 51
60 PPM- - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 52
30 PPM- - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 57
9 PPM  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 62
7 PPM  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 69
Boiler Controls And Control Panel   - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 74
Flue Gas Heat Recovery (Optional Selection)  - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 74
Efficiency Guarantee   - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 74
EXECUTION
Warranty - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 74
Shop Tests   - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - - 74
SAMPLE SPECIFICATIONS
The following sample  specifications  are provided by Cleaver-Brooks to assist  you in meeting  your customer's specific needs and application.
The Sample  Specifications  are  typically utilized as  the  base  template  for the  complete  boiler specification. Contact your local Cleaver-Brooks authorized representative  for information on special insurance  requirements, special code requirements, optional equipment, or general assistance in completing the specification.
PART 1 
GENERAL
CBEX Hot Water Boiler 100-800 HP
4.1 
BOILER CHARACTERISTICS (HOT WATER)
A.
The boiler shall be Cleaver-Brooks Fuel Series  
(100, 200, 700),  
hp designed for
 
psig (30, 125, or other) hot water. The maximum operating pressure shall be  

psig and the minimum operating pressure shall be  
psig.
B. 
The boiler shall have a maximum output of  

Btu/hr, or  
horsepower when fired with CS12-48 #2 oil and/or natural gas,  
Btu/cu-ft. Electrical power available shall be
 
Volt  
Phase  
Cycle.
PART 2 
PRODUCTS
5.1 
GENERAL BOILER DESIGN
A.
Design shall be optimized using CFD modeling verifiable by manufacturer. The boiler shall be a multipass  pass horizontal firetube updraft boiler with using extended heating surface optimized to reduce boiler foot print. Boiler shall be mounted  on a heavy steel frame with integral forced draft burner and burner controls.
1. 
The boiler shall be completely preassembled and fire tested  at the factory. The unit shall be ready for immediate mounting on floor or simple foundation and ready for attachment of water, fuel, electrical, vent, and blowdown connections.
2. 
The boiler shall be built to comply with the following insurance and codes (Factory Mutual, XL GAP, ASME, NFPA 8501).
B. 
Boiler Shell (Hot Water)
1. 
The boiler shell must be constructed  in accordance  with ASME boiler code and must receive authorized boiler inspection prior to shipment. A copy of the inspection report shall be furnished to the purchaser.
2. 
The hot water return and outlet connections  shall be located on the top center line of the boiler. The boiler shall be designated  to rapidly mix the return water with the boiler water. Forced internal circulation shall be used.
3. 
A dip tube shall be included as an integral part of the water outlet.
4. 
The boiler shall be furnished with a manhole  and handholes  to facilitate boiler inspection and cleaning. Two lifting lugs must be located on top of the boiler.
5. 
The front smokebox doors shall be davited and sealed with superwool insulation and fastened tightly using locking lugs on steel studs.
6. 
The rear head shall be fitted with an access  plug for rear fireside inspection.
7. 
The boiler tubes shall not include turbulators,  swirlers, or other add-on appurtenances.
8. 
The exhaust gas vent shall be located at the front of the boiler and be capable  of supporting 2000 lbs. The boiler vent shall contain a stack thermometer.
9. 
Observation ports for the inspection of flame conditions shall be provided at each end of the boiler.
10.   The boiler insulation shall consist of 2 inch blanket under a sectional pre-formed sheet metal lagging. The insulation must be readily removable and capable of being reinstalled if required.
11.   The entire boiler base frame and other components  shall be factory painted  before shipment, using a hard-finish enamel coating.
12.   The boiler shall contain a chemical feed connection.
5.2 
HOT WATER BOILER TRIM
A.
Low Water Cutoff - A low water cutoff control (manual reset) shall be mounted  on the top centerline of the boiler wired into the burner control circuit to prevent burner operation if boiler water falls below a safe level.
B. 
Pressure  and Temperature  Gauges - Pressure  and temperature gauges shall be mounted  on the boiler with temperature sensing element located adjacent  to the hot water outlet.
C.
Relief Valves - Water relief valves of a type and size to comply with ASME Code requirements shall be shipped  loose.
D.
Temperature  Controls - Temperature  controls to regulate burner operation shall be mounted  on the unit with temperature sensing elements  located adjacent  to the hot water outlet. Controls shall be high limit (manual reset), operating limit (auto reset), and firing rate control.
5.3 
BURNER
A.
Burner shall incorporate Cleaver Brooks “Lean Burn Technology”.
B. 
Fuel and air ratio/mixture shall be controlled over the entire operating range, allowing for firing at constant  excess air on high turndown burner application.
C.
Burner to be designed specifically for boiler including optimized furnace allowing for low emissions and lean burn combustion.
D.
Mode of Operation
1. 
Burner operation shall be full modulation principle. The burner shall always return to low fire position for ignition.
2. 
A low fire hold temperature control is mounted  and wired on the boiler. E. 
Blower
1. 
Air for combustion  shall be supplied by a forced draft blower incorporated  into the burner design to eliminate vibration and reduce noise level.
2. 
Maximum sound level of the boiler/burner package shall not exceed  
dbA (when measured  in accordance  with ABMA Sound Test Standards).
3. 
The impeller shall be fabricated aluminum  with radial blade, carefully balanced, and directly connected  to the blower motor shaft.
F. 
Combustion Air Control
Combustion air damper  and fuel metering valve shall be operated  by individual actuators  to regulate the flame according to load demand.
5.4 
FUEL SPECIFICATION AND PIPING
Select one of the following fuel types:
• Fuel series 700  - Gas-fired.
• Fuel series 100  - Light oil (No. 2) fired .
• Fuel series 200  - Light oil or gas-fired.
NOTE: Specification writer to select  between  NOx options of 60  ppm, 30  ppm, 9 ppm or 7 ppm Nox on Natural Gas as required for specific project conditions.
60  PPM Nox Operation Natural Gas
CBEX 100 to 200 Horsepower 60 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 4:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5. 
CO on Natural Gas is 10 ppm at 50,  75 and 100  % of firing and 25 ppm at 25%  firing rate. Excess air is 15%  at 50,  75 and 100% of firing and 30%  at 25%  firing rate.
B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 4:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 4:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 4:1  when firing natural gas.
c. 
CO on Natural Gas is 10 ppm at 50,  75 and 100  % of firing and 25 ppm at 25% firing rate. Excess air is 15%  at 50,  75 and 100% of firing and 30%  at 25%  firing rate.
CBEX 250 and 300 Horsepower 60 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 10:1 when firing natural gas. VSD required to maintain  3% O2 over turndown range.
5. 
CO on Natural Gas is 10 ppm with excess air at 15%  in firing range of 50%  to 100%
increasing to 50 ppm CO at 10:1  turndown.
B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 7:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 7:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
a.Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test Gconnection. The main gas valve shall be wired to close automatically in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 10:1 with 15%  excess air when firing natural gas. VSD required to maintain  3% O2 over turndown range.
c. 
CO on Natural Gas is 10 ppm at 50%  to 100% firing increasing to 50 ppm CO at
10:1 turndown.
CBEX 350 to 800 Horsepower 60 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 10:1 with 15% excess air across the turndown range. VSD required to hold excess air across firing range on natural gas.
5. 
CO on Natural Gas is 10 ppm with excess air at 15%. B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 8:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 8:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating
plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 10:1 when firing natural gas with 15% excess air over the turndown range. VSD required to maintain  excess air over turndown range.
c. 
CO on Natural Gas is 10 ppm with excess air at 15%.
30  PPM Nox Operation Natural Gas
CBEX 100 to 200 Horsepower 30 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 4:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5. 
CO on Natural Gas is 25 ppm at 50,  75 and 100  % of firing and 50 ppm at 25%  firing rate. Excess air is 15%  at 50,  75 and 100% of firing and 30%  at 25%  firing rate.
B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 4:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 4:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 4:1  when firing natural gas.
c. 
CO on Natural Gas is 25 ppm at 50,  75 and 100  % of firing and 50 ppm at 25% firing rate. Excess air is 15%  at 50,  75 and 100% of firing and 30%  at 25%  firing rate.
CBEX 250 and 300 Horsepower 30 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 10:1 when firing natural gas with 15% excess air across the firing range. VSD required to hold 15%  excess air across the firing range.
5. 
CO on Natural Gas is 10 ppm with excess air at 15%,  from 50%  to 100% firing. CO will increase to 50 ppm at 10:1 turndown.
B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 7:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
b. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
c. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
d. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
e. 
 Burner Turndown - Turndown range shall be 7:1  when firing No. 2 oil. f. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 10:1 when firing natural gas with 15%
excess air over the turndown range. VSD required to hold excess air over turndown.
c. 
CO on Natural Gas is 10 ppm with excess air at 15%  from 50%  to 100% firing. CO
will increase to 50 ppm at turndown of 10:1.
CBEX 350 to 800 Horsepower 30 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 10:1 with 15% excess air across the turndown range. VSD required to hold excess air across firing range on natural gas.
5. 
CO on Natural Gas is 10 ppm with excess air at 15%. B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 8:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 8:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 10:1 with 15%  excess air across the turndown range. VSD required to hold excess air across firing range on natural gas.
c. 
CO on Natural Gas is 10 ppm with excess air at 15%.
9 PPM Nox Operation Natural Gas
CBEX 100 to 200 Horsepower 9 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 4:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5. 
CO on Natural Gas is 25 ppm with excess air at 25%.
B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 4:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 4:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and
low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 4:1  when firing natural gas. c. 
CO on Natural Gas is 25 ppm with excess air at 25%.
CBEX 250 to 400 Horsepower 9 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 5:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5. 
CO on Natural Gas is 25 ppm with excess air at 25%. B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 5:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 5:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 5:1  when firing natural gas. c. 
CO on Natural Gas is 25 ppm with excess air at 25%.
CBEX 500 and 600 Horsepower 9 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 6:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5. 
CO on Natural Gas is 25 ppm with excess air at 25%. B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 6:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 6:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 6:1  when firing natural gas. c. 
CO on Natural Gas is 25 ppm with excess air at 25%.
CBEX 700 and 800 Horsepower 9 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be  7:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5. 
CO on Natural Gas is 25 ppm with excess air at 25%.
B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 7:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 7:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High
and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 7:1  when firing natural gas. c. 
CO on Natural Gas is 25 ppm with excess air at 25%.
7 PPM Nox Operation Natural Gas
CBEX 100 to 200 Horsepower 7 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 3:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5. 
CO on Natural Gas is 50 ppm with excess air at 30%. B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 3:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, b. and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 3:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 3:1  when firing natural gas. c. 
CO on Natural Gas is 50 ppm with excess air at 30%.
CBEX 250 to 500  Horsepower 7 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be 4:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5.
CO on Natural Gas is 50 ppm with excess air at 30%.
B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 4:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 4:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 4:1  when firing natural gas. c. 
CO on Natural Gas is 50 ppm with excess air at 30%.
CBEX 600 to 800 Horsepower 7 PPM
A.
Fuel Series 700  - Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be of high radiant multi-port type gas entry. Burner shall be approved for operation on natural gas fuel.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary gas valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection. The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown  condition. A lubricating plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches  shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
4. 
Burner Turndown: Turndown range shall be  5:1  when firing natural gas (consult with Cleaver-Brooks representative  regarding high turndown capability based  on available gas pressure).
5. 
CO on Natural Gas is 50 ppm with excess air at 30%. B. 
Fuel Series 100  - Light Oil-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a low pressure air atomizing type approved for operation with CS12-48 Commercial No. 2 oil.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary oil valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, to be installed in a location favorable to the oil storage tank, shall be provided.
4. 
Oil Burner Piping
a. 
Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves and pressure gauges, all integrally mounted  on the unit.
5. 
Low Pressure  Air Atomizing: separate  air compressor  module, shipped  loose, with burner mounted  low atomizing air pressure switch.
6. 
Turndown range shall be 5:1  when firing No. 2 oil.
7. 
Excess air is 25%  with 10 ppm CO.
C.
Fuel Series 200  - Light Oil or Gas-Fired
1. 
Burner type - The burner shall be mounted  at the front of the boiler and shall be a combination of the low pressure air atomizing type for oil and multi-port type for gas. The burner shall be approved for operation with either CS12-48 Commercial No. 2 oil or natural gas.
2. 
Gas Pilot - The gas pilot shall be a premix type with automatic  electric ignition. An electronic detector shall monitor the pilot so that the primary fuel valve cannot open until pilot flame has been established. The pilot train shall include one manual  shut-off valve, solenoid valve, pressure regulator and one (1) plugged leakage test connection (Canada only).
3. 
Oil Burner
a. 
Oil Pump - An oil pump with a capacity of approximately twice the maximum burning rate shall be included. The motor-driven pump set, shipped  loose, shall be provided, to be installed in a location favorable to the oil storage tank.
b. 
Oil Burner Piping - Fuel oil piping on the unit shall include oil pressure regulating devices, oil metering controls, low oil pressure switch, two (2) motorized oil valves, and pressure gauges all integrally mounted  on the unit.
c. 
Low pressure air atomizing - Separate  air compressor  module, shipped  loose with burner-mounted  low-atomizing air pressure switch.
d. 
Burner Turndown - Turndown range shall be 5:1  when firing No. 2 oil. e. 
Excess air is 25%  with 10 ppm CO.
4. 
Gas Burner
a. 
Gas Burner Piping - Gas burner piping on all units shall include a primary gas shutoff valve, motor operated  with proof of closure switch and plugged leakage test connection.  The main gas valve shall be wired to close automatically  in the event of power failure, flame failure, low water or any safety shutdown condition. A lubricating
plug cock shall be provided as a means  for a tightness  check of the primary shutoff valve. An additional plug cock shall be furnished at entrance  to gas train. High and low gas pressure switches shall be provided. A second motorized safety shutoff valve with plugged leakage test connection shall be provided. A vent valve shall be located between the safety shutoff valves. Gas pressure regulator can be offered as an option.
b. 
Burner Turndown - Turndown range shall be 5:1  when firing natural gas. c. 
CO on Natural Gas is 50 ppm with excess air at 30%.
5.5 
BOILER CONTROLS AND CONTROL PANEL
A.
Control/Entrance Panel - A common enclosure shall house the control panel and the entrance panel. Enclosure shall be NEMA 4/12  rated and shall be mounted  at the side of the boiler in a location convenient to the operator. Enclosure shall consist of upper and lower sections divided by a partition with a separate  hinged door for each section. Upper section (low voltage) will house boiler controls including flame safeguard and water level system controller. Lower panel section (high voltage) will house entrance  panel.
B. 
Cleaver Brooks Combustion Control System - Hawk 2000 with parallel positioning with separate actuators  for each fuel and combustion  air shall be used to provide proper fuel air ratio control.
C.
CB780E Flame Safeguard - Each boiler shall be factory equipped  with flame safeguard controller incorporated  into the Hawk control.
Oil, heat  and  moisture  resistant  wire shall be used  and  identified with circuit numbers  corresponding  to the electrical wiring diagram.
Boiler to be supplied with a control circuit transformer and fuse protection for the control circuit.
5.6 
FLUE GAS HEAT RECOVERY (OPTIONAL SELECTION)
A.
Add Cleaver Brooks economizer selection in this area.
B. 
Boiler and economizer to be designed with integral supports  allowing for easy economizer installation on boiler eliminating the requirement  for separate  structure  steel support.
5.7 
EFFICIENCY GUARANTEE
A.
The boiler must be guaranteed to operate at a minimum fuel-to-water efficiency of  

percent at 100% of rating when burning natural gas and  
fuel-to-water efficiency at
100% firing rate when burning oil (Contact your local Cleaver-Brooks authorized representative for efficiency details).
PART 3 
EXECUTION
6.1 
WARRANTY
A.
All equipment  is to be guaranteed against defects in materials  and/or workmanship  for a period of 12 months  from date of start-up,  or 18 months  from date of shipment;  whichever comes first.
6.2 
SHOP TESTS
A.
The packaged  boiler must receive factory tests to check the construction,  controls, and operation of the unit. All tests may be witnessed  by the purchaser, if desired.
B. 
Start-up Service
1. 
After boiler installation is completed,  the manufacturer  shall provide the services of a field representative  for starting the unit and training the operator at no additional costs.
2. 
A factory-approved and authorized start-up report shall be submitted  to the customer/user at the time of start-up.



