[image: image1.png]CLEAVER '’BROOKS



Model (ie. Model CFV)


Group (ie. Commercial Boilers

[image: image2.png]CleaverBrooks’ b



Model Intermediate Level Control Single Tank
LCS150e.1

Sample Specifications

CB LCS-150E.1 Level Control System
1.1 GENERAL 
General
A.
Each LCS-150E.1 system shall be factory equipped with controller including display and I/O, NEMA 12 cabinet, primary and optional secondary make up valves and GEMS magnetic level sensor with transmitter.
B. 
System shall provide the following functions:

1. 
Adjustable transmitter span

2. 
Individual adjustable water level set point for each MUV

3. 
Adjustable high-high water alarm point (with differential)

4. 
Adjustable high water alarm point (with differential)

5. 
Adjustable low water alarm point (with differential)

6. 
Adjustable low-low water alarm point (with differential)

7. 
Adjustable low water cutoff point (with differential)

8. 
Adjustable P and I (proportional and integral gain) parameters

9. 
Manual or automatic make-up valve operation

10. 
On-screen alarm indication and relay outputs for high water, low water, low water cutoff, and general alarms

11. 
Alarm Silence input

12. 
On-screen trending, Modbus RTU communications and data logging to an optional micro SD card.
2.1 PRODUCTS
Standard System

A.
Hardware Platform
1. 
Controller with backlit graphic display

2. 
Power Supply 115VA/24VDC 30 Watts

3. 
I/O module:
(12) 24VDC inputs

(12) 24VDC outputs

 (2) 4-20 mA analog output for 2 make-up valves
(1) 4-20 mA input for a level transmitter

B. 
Level sensor and transmitter

1. 
GEMS Mini Sure Site magnetic level indicator

2. 
Level transmitter 4-20 mA 
C.
Make-up valve

1. 
Siemens modulating feed water valve - sized per application

2. 
Electronic actuator 4-20 mA.
D.
Alarms
1. 
Panel mounted alarm horn

2. 
Alarm silence switch

3. 
LED alarm lights for High-High, High, Low, Low-Low and Low Water Cut- Off
4.
Customer Relay contacts for High-High, High, Low, Low-Low and Low Water Cut-Off


















�











Section (ie. B9)-Page #
Rev. date (ie. Rev. 11-10)
Section D06-1
Rev. 03-11

